Section Cover Page

Section 09 69 00 2014-11-01 Access Flooring

Refer to “LEED Notes and Credits” page for additional guidance for LEED projects. Delete LEED items if project: .1 is excluded by the Department’s policy on LEED, or .2 the Department has determined that the work of this Contract is not to attain a LEED rating.

Use this section to specify "elevated" or "raised" access flooring systems.

This Master Specification Section contains:

.1	This Cover Sheet

.2	LEED Notes and Credits

.3	Data Sheet – General

.4	Specification Section Text:

1.	General

1.1	Related Work Specified in Other Sections

1.2	Reference Documents

1.3	Product Options and Substitutions

1.4	Description of System

1.5	Installer Qualifications

1.6	Performance and Design Requirements

1.7	Submittals

1.8	Closeout Submittals

1.9	Maintenance Material Submittals

1.10	Quality Assurance

1.11	Delivery, Storage, and Handling

2.	Products

2.1	Product Manufacturers

2.2	Pedestals

2.3	Steel Floor Panels

2.4	Composite Steel Floor Panels

2.5	Aluminum Floor Panels

2.6	Stringers

2.7	Vinyl Seal

2.8	Ramps [and Steps]

2.9	Fascia Panels

2.10	Railings and Posts

2.11	Base

2.12	Accessories

2.13	Metal Finishes

  - Flooring Finishes

3.	Installation

3.1	General

3.2	Pedestals and Stringers

3.3	Floor Panels

3.4	Fascia Panels

3.5	Railings

3.6	Plenum Dividers

3.7	Base

3.8	Grounding

3.9	Protection of Finished Work

3.10	Schedule

LEED Notes:

If the project is not a designated LEED project, but is following sustainable building practices, specify that adhesive products meet SCAQMD Rule #1168, or meet CRI Green Label or Green Label Plus. Also specify carpet and under-cushion to have CRI Green Label or Green Label Plus.

Raised access flooring manufacturers tend not to have ‘green’ flooring products as part of their ‘standard’. As a result the LEED credit for carpet, (MEQ 4.3), may be un-obtainable even if there is only a small portion of the building that had access flooring. A solution to this problem would be to have the access flooring manufacturer only provide the metal system and then specify carpet tile under Section 09 68 18 to meet the Green Label performance standard.

LEED Credits:

Contribution towards LEED credits in this section may apply as follows:

1.	LEED Credit MR 4: Recycled Content. Flooring as well as the metal components of access flooring may apply.

Investigate whether or not the manufacturer of access flooring may have recycled content in the flooring product and the metal components.

The criteria is that the sum of post-consumer recycled content plus one-half of the pre-consumer content constitutes at least the percent(10% and 20%)of the total value of the materials in the project.

2.	LEED Credit EQ 4.1 Low-Emitting Materials: Sealants and Adhesives. Adhesives specified under this section apply.

In order to obtain EQ 4.1, VOC content in adhesives must be less than the VOC content limits of the State of California’s South Coast Air Quality Management District (SCAQMD) Rule #1168, June 2006.

3.	LEED Credit EQ 4.3 Low-Emitting Materials: Flooring Systems. Carpets specified under this section will apply if they have the CRI Green Label.

In order to obtain EQ 4.3, carpet systems must meet or exceed the requirements of the Carpet and Rug Institutes(CRI) Green Label Indoor Air Quality Test Program. Manufacturer’s will be required to submit product data and information verifying compliance.

Verify design requirements to include for:

.1	Stairs, ramps and railings.

.2	Excessive floor loading.

.3	Cable cutouts.

.4	When flooring system must be sealed as a plenum, check for plenum dividers and zoning divisions.  Verify and coordinate plenum requirements with mechanical sections.

When the underfloor cavity is an air distribution plenum for electronic data processing equipment, ensure that potential sources of dust such as unsealed concrete are eliminated to the extent possible.

Floor coverings and bases are available in a wide range of materials and applications.  Refer to applicable sections of Division 09 for detailed specifications for materials to be included in this section.

1.	General

1.1	RELATED WORK SPECIFIED IN OTHER SECTIONS

.1	[LEED Submittal Forms	Section 01 32 16.]

.2	[LEED Requirements	Section 01 35 18.]

.3	[Environmental Procedures	Section 01 35 20.]

.4	Waste Management and Disposal	Section 01 74 19.

.5	Ventilation and related mechanical work:	Division 23.

.6	Grounding and related electrical work:	Division 26.

1.2	Reference Documents

SPEC NOTE: Edit this article to include only standards referenced within the edited version of this Section, including LEED documentation and sustainable practices.

.1	Aluminum Association (AA)

| .1 | DAF 45-[03] | Designation System for Aluminum Finishes |
| --- | --- | --- |

.2	Canada Green Building Council (CaGBC)

| .1 | LEED Canada 2009 Rating System | LEED Canada for New Construction and Major Renovations. LEED Canada for Core and Shell Development. Website: www.cagbc.org |
| --- | --- | --- |

.3	Canadian General Standards Board (CGSB)

| .1 | CAN/CGSB 1.81-M90 AMEND | Air Drying and Baking Alkyd Primer for Vehicles and Equipment |
| --- | --- | --- |
| .2 | CAN/CGSB 1.88-92 | Gloss Alkyd Enamel, Air Drying and Baking |
| .3 | CAN/CGSB 1.104-M91 | Semigloss Alkyd Air Drying and Baking Enamel |
| .4 | CAN/CGSB-4.129-93 AMEND | Carpet for Commercial Use |
| .5 | CAN/CGSB 51.34-M86 AMEND | Vapour Barrier, Polyethylene Sheet for Use in Building Construction |

.4	Canadian Standards Association

| .1 | CAN3-A172-M79(R1996) | High Pressure Paper Base, Decorative Laminates |
| --- | --- | --- |

.5	South Coast Air Quality Management District (SCAQMD), California State (SCAQMD)

| .1 | SCAQMD Rule 1168, June 2006 | Adhesives and Sealants Applications |
| --- | --- | --- |

.6	Underwriters Laboratories of Canada (ULC)

| .1 | CAN/ULC S102-07 | Standard Method of Test for Surface Burning Characteristics of Building Materials and Assemblies |
| --- | --- | --- |
| .2 | CAN/ULC S102.2-07 | Method of Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies |

1.3	PRODUCT OPTIONS AND SUBSTITUTIONS

.1	Refer to Division 01 for requirements pertaining to product options and substitutions.

1.4	DESCRIPTION OF SYSTEM

.1	General Description:  Raised, adjustable access flooring system consisting of support system, interchangeable flooring panels, finished flooring, bases associated components and accessories.

.2	Dimensions:

.1	Horizontal Module:  [           ].

.2	Height:  [    ] mm to [    ] mm.

.3	Vertical Adjustability:  [     ] mm.

.3	Support System:

.1	Pedestals

.2	Removable stringer grid, [unexposed] [exposed].

[OR]

.2	Fixed stringer grid, [unexposed] [exposed].

[OR]

.2	Stringerless (no grid).

.4	Pedestals:

.1	Adjustable [Steel] [or] [Aluminum]

.5	Floor Panels - one of the following:

.1	Steel.

.2	Aluminum.

.3	Composite wood and metal.

.6	Floor Panel Finish:

.1	Carpet.

.2	Vinyl Asbestos Tile.

.3	Non-slip Rubber.

.4	Melamine phenolic laminate.

.5	Homogenous vinyl sheet.

.6	[                         ].

.7	Accessibility:

.1	All floor panels removable.

.2	Full size panels interchangeable.

.3	Panel lifting device to suit floor covering.

1.5	INSTALLER QUALIFICATIONS

.1	Installation of access floor shall be an applicator authorized by manufacturer of system being installed.

1.6	PERFORMANCE AND DESIGN REQUIREMENTS

.1	Evenness of Surface:

.1	Maximum variation 1:2000 over entire floor.

.2	Strength:

.1	Twice design strength minimum.

.2	Complete rigid assembly when eight abutting panels are removed.

.3	Pedestals:

.1	Maximum axial load:  [22] kN with no deflection.

.2	Ultimate load carrying capacity:  not less than twice design strength.

.4	Adhesive Strength:

.1	Minimum 178 N horizontal force applied to 300 mm high pedestal without bond impairment.

.5	Floor panels:

.1	Live load [12] kN/m2:  maximum deflection [1] mm.

.2	Concentrated load [7] kPa at any location:  maximum deflection [2] mm.

.3	Permanent deflection:  maximum [0.5] mm at design load.

.6	Allowable component tolerances:

.1	Floor panel flatness:  ± [0.5] mm in any direction.

.2	Floor panel surface dimension:  ± [0.5] mm.

.3	Floor panel squareness:  ± [0.5] mm in panel surface dimension and [0.25] mm measured diagonally.

.7	Surface electrical resistance not to exceed [2 x 1010] ohms nor be less than [5 x 105] ohms.

SPEC NOTE:  Verify surface electrical resistance requirements, of equipment to be installed.  Coordinate resistance values with floor finish.

1.7	Submittals

.1 	Product Data:

.1	Submit manufacturer’s printed product literature, specifications and data sheets in accordance with Section 01 33 00 - Submittal Procedures.

.2	Submit WHMIS MSDS - Material Safety Data Sheets acceptable to Labour Canada and Health Canada for flooring adhesive.  Indicate VOC content.

.3	Submit data on specified products, describing physical and performance characteristics, sizes, patterns, colours, and methods of installation.

.4	Submit verification to demonstrate compliance with [CAN/ULC S102] [and] [CAN/ULC S102.2].

.2	Shop Drawings:

.1	Comply with requirements of Division 01.

.2	Indicate:

.1	Floor panel layout.

.2	Component details.

.3	Anchorage methods.

.4	Edging details.

.5	Elevation differences.

.6	Fascias, step, ramp and handrail details.

.7	Grilles, registers and perforated panels.

.3	Samples:

.1	Comply with requirements of Division 01.

.2	Submit [duplicate] samples of:

.1	[200 x 300] mm of each floor covering type, colour, pattern and finish.

.2	[300] mm long cove base.

.4	Certificates:

.1	Submit certificates provided by an independent nationally recognized testing organization certify:

.1	Specified design strengths.

.2	Flame spread ratings.

.3	Electrical resistances.

.5	Sustainable Design Submittals:

.1 	Green Label Program Submittals:

SPEC NOTE: Delete the following requirement for Green Label Program if project is attaining LEED certification as this submittal is listed further below under LEED Submittals. Also, edit for Green Label or Green Label Plus as required for project.

.1	Submit proof that carpet meets or exceeds the requirements of the Carpet and Rug Institutes(CRI) [Green Label][Green Label Plus] Indoor Air Quality Test Program and the Canadian Carpet Institute (CCI).

SPEC NOTE: Use the following paragraph when LEED Submittals are required:

.2	LEED Submittals: Submit documentation in accordance with Section 01 35 18 – LEED Requirements.  Submit documentation for the following:

SPEC NOTE: Delete LEED submittal item if project is not to attain LEED certification or if Credit MR 4.1and/or 4.2 are not being sought.

.1	Materials & Resources:

.1	MR Credit 4 - Recycled Content: [10%] [20%] (post-consumer + ½ pre-consumer)

.2	Indoor Environmental Quality:

SPEC NOTE: Delete LEED submittal item below if project is not to attain LEED certification or if Credit EQ 4.1 Low Emitting Materials: Adhesives and Sealants is not being sought. If project is to follow sustainable building practices but not attaining LEED certification, delete references to LEED and retain SCAQMD Rule #1168 as a sustainable submittal.

.1	EQ Credit 4.1 - Low-Emitting Materials: Adhesives & Sealants

SPEC NOTE: Delete LEED submittal item below if project is not to attain LEED certification or if Credit EQ 4.3 Low Emitting Materials: Flooring Systems, is not being sought. Also edit for Green Label and Green Label Plus as required for project.

.2	EQ Credit 4.3 - Low-Emitting Materials: Flooring Systems

1.8	closeout submittals

.1	Operation and Maintenance Data:

.1	Submit maintenance data for flooring products in accordance with Section 01 78 23 – Operation and Maintenance Data and Manuals.

.2	Include data in Maintenance Manual for maintenance of:

.1	Floor finishes.

.2	Access flooring systems and components.

1.9	MAINTENANCE MATERIAL Submmittals

.1	Extra Stock Materials:

.1	Provide [         ] spare floor panels.

.2	Provide [         ] spare pedestals, associated stringers and components.

.3	Provide [       ] panels of finished floor materials, of same production run as installed materials.

.4	Identify each carton of materials.

.5	Store where directed.

SPEC NOTE:  Check requirements for maintenance materials and storage availability with maintenance forces.  On larger projects, it is suggested 2%-5% of installed material area be allowed for maintenance purposes.  Include 1.7 only if Access Flooring supplier is providing finished flooring.

1.10	quality assurance

.1	Qualifications:

.1	Installers / Applicators / Erectors

.1	Installation of access floor shall be an applicator authorized by manufacturer of system being installed.

.2	Mock-Ups:

.1	Site assemble an 1800 mm x 1800 mm of access flooring where directed.

.2	Obtain Province's approval of mock-up before starting installation.

SPEC NOTE:  Verify project needs.  Delete 1.6.2 when finished flooring is specified in another specification section.

1.11	delivery, storage, and handling

.1	Waste Management and Disposal:

.1	Separate waste materials for [reuse] [and] [recycling] in accordance with Section 01 74 19 – Management and Disposal.

2.	Products

2.1	PRODUCT MANUFACTURERS

SPEC NOTE:  Include 2.1 only when the use of a proprietary specification is deemed essential.  Normally this article will not be required.

.1	Access Flooring System:  by one of the following:

.1	[Manufacturer's Name, Address, etc.], [Model no. etc.].

.2	[                                  ], [              ].

.3	[                                  ], [              ].

.4	[                                  ], [              ].

.2	Substitutions will not be accepted.

SPEC NOTE:  Specify 2.1.2 above only  when the named manufacturers meet project requirements.  This must be approved by Specifications and Standards Section.

2.2	PEDESTALS

.1	[Steel] or [Aluminum].

.2	Base Plates:  10,000 mm2.

.3	Threaded supporting rod, vibration proof locknut, 38 mm minimum adjustment.

.4	Manufacturer's standard [galvanized] finish.

.5	Adjustable from horizontal plane 4°, to compensate for uneven sub-floor.

2.3	STEEL FLOOR PANELS

.1	[          ] mm x [        ] mm.

.2	Die formed.

.3	Bottom Plate  reinforced steel welded to flat steel die cut top plate.

.4	Manufacturer's standard [Baked Enamel] finish.

2.4	COMPOSITE STEEL FLOOR PANELS

.1	[     ] mm x [    ] mm.

.2	[Particle board] or [plywood] core.

.3	Galvanized sheet steel skin bonded to all faces of core with thermosetting adhesive.

2.5	ALUMINUM FLOOR PANELS

.1	[     ] mm [     ] mm.

.2	Die cast:  rough spots and cast imperfections removed, edges machined.

SPEC NOTE:  Select panel construction from 2.3, 2.4 or 2.5 if required.

2.6	STRINGERS

.1	Continuous or removable type.

.2	[Steel] or [Aluminum].

.3	Shaped to receive integrally extruded vinyl seal on top surface.

2.7	VINYL SEAL

.1	Located on stringers or floor panels.

.2	Electrically conductive.

.3	Shaped to seal off air plenum under finished access floor panels.

2.8	RAMPS [AND STEPS]

.1	Same materials, structural strength and construction as floor panels.

.2	Cover open joints with flush [aluminum] or [stainless steel] cover plates.

2.9	FASCIA PANELS

.1	Construction and finishes to match floor panels.

.2	Include corner pieces, trim, reinforcing and fixing angles required.

2.10	RAILINGS AND POSTS

.1	[Extruded aluminum] or [galvanized steel].

.2	[Welded] [Sleeved] connections.

.3	Include cast metal end caps, floor sockets, collars, brackets and fittings required.

.4	[Anodized] [Baked enamel] manufacturer's standard finish.

2.11	BASE

.1	Extruded [vinyl] [rubber] with preformed corners.

.2	[63] [100] [150] mm high.

.3	Colour [indicated on finish schedule] [selected by Province from manufacturer's standard range].

SPEC NOTE:  Delete base if specified to be supplied and installed in other flooring Sections.

2.12	ACCESSORIES

.1	Panel lifting device:

.1	[1] [2] per enclosed area.

.2	Type recommended for each panel type.

.3	Manufacturer's standard design.

.2	Perforated floor panels:

.1	Same size, materials and construction as floor panels. [with slide damper].

.2	[10] [   ]% free area.

.3	Air grilles:

.1	[    ] mm x [     ] mm.

.2	Live load design  [4.8] [    ] kN/m2.

.3	[Straight] [Deflecting] vanes.

.4	Shutoff damper.

.5	[Galvanized sheet steel with baked enamel finish] [anodized extruded aluminum].

.4	Grounding connectors:  solid copper.

SPEC NOTE:  Delete VOC content requirement below if project is not attaining LEED certification or LEED Credit EQ 4.1 is not being sought, or otherwise not applying sustainable building practices.

.5	Adhesives: as recommended by flooring manufacturer for each flooring material on applicable substrate, [moisture resistant] [waterproof] [electrically conductive] [VOC content compliant with SCAQMD Rule #1168, June 2006].

.6	Cable cutout protection:

.1	[Extruded polyvinyl chloride] or [neoprene edging] or [closed cell neoprene sheet].

.2	[9.5] [     ] mm thick.

.3	Self-extinguishing and non-burning.

.7	Plenum divider:

.1	Galvanized sheet steel.

.2	0.46 mm thick to 330 mm high.

.3	0.6 mm thick above 300 mm high.

.8	Trim:  to match finish floor [and fascia panels] except where noted otherwise.

.9	Polyethylene sheet:  to CAN/CGSB-51.33-M89, Type 2.

2.13	METAL FINISHES

.1	Aluminum components:

.1	Provide mechanical, chemical and anodic finishes in accordance with Aluminum Association Designation System for Aluminum Finishes-1973.

.2	Steel components:

.1	Exposed steel components:

.1	Painted:  [Gloss] [Semi-gloss].

.2	Colour selected by Province from manufacturer's standard range.

.2	Concealed steel components:  1 coat baked primer.

SPEC NOTE:  Delete concealed paint finish if not required.

2.14	FLOORING FINISHES

SPEC NOTE:  Determine if Access Flooring Manufacturer is to provide the chosen floor finishes.

.1	Factory applied [3] mm thick, vinyl asbestos tile.

.2	Factory applied [3] mm thick homogenous vinyl [tile] [sheet].

.3	Factory applied [3] mm thick, melamine phenolic laminate to CAN3-A172 designed for floor panel use.

SPEC NOTE: Delete the CRI requirement below if project is not attaining LEED Certification or not seeking Credit MR 4.3, or otherwise not applying sustainable building practices. Also, choose either Green Label or Green Label Plus. Determine if the manufacture’s standard meets Green Label requirements. If it does not the project will not be able to obtain Credit MR 4.3.

.4	Provide carpet that meets or exceeds the Carpet and Rug Institutes(CRI) [Green Label][Green Label Plus] Indoor Air Quality Test Program.][to CAN/CGSB-4.129][manufacturer’s standard].

SPEC NOTE:  Refer to 09 68 17 for detailed specification.  When reference is made to CAN/CGSB 4.129-93 specify pile fibre, cushion backing, static control, medium or heavy traffic conditions. Consult with Access Flooring manufacturer.

.5	Factory applied [3] mm thick ribbed, non-slip rubber flooring.

SPEC NOTE:  Specify finish floor materials from list 2.14.1 to 2.14.4.  If more than one material is required for a project, specify locations.

.6	Finish panel edges with vinyl trim.

3.	Installation

3.1	GENERAL

.1	Install components to system manufacturer's instructions.

3.2	PEDESTALS AND STRINGERS

.1	To meet grid spacing required.

.2	Bond pedestals base plate to structural floor with adhesive.

.3	Install additional pedestal assemblies where required to maintain load capacity.

.4	Brace floor pedestals four ways with stringers.

3.3	FLOOR PANELS

.1	Install [grilles] [perforated panels] where indicated.

.2	Install [ramp] [and] [step tread] panels similar to floor panels, securely fixed.  [Include shoe at top and bottom of ramp].

.3	Seal field cuts with plastic angles or channels.  No exposed cut edges permitted.

.4	Install required edge trims, end closures.

.5	Allow for cutting [        ] hundred [       ] mm dia. holes in floor panels for installation of equipment [and air conditioning units].  Include cable protection edging or sheet.

3.4	FASCIA PANELS

.1	Install fascia panels at:

.1	Exposed sides.

.2	Ramp sides.

.3	Step risers.

.4	Where indicated.

.2	Secure panels to continuous clip angles.  Mechanically Secure to structural floor and to edge of floor panels.

.3	Install metal trim at intersection of fascia panels and access floor [and at abutting walls and columns].

3.5	RAILINGS

.1	Extend railing posts through floor panels.

.2	Secure to structural floor below with bolted flanged fittings.

.3	Bolt posts in position at floor panels with retaining floor collar.

.4	Set wall railings into flanged fittings bolted to walls.

.5	Electrically insulated or directly ground to access flooring system.

3.6	PLENUM DIVIDERS

.1	Install positive air seal between sub-floor and elevated floor.

.2	Install sponge rubber cut-out panels at wiring holes in plenum.

SPEC NOTE:  Ensure drawings indicate number and locations of plenum dividers.

3.7	BASE

.1	Bond base along intersection of walls and access floor panels.

SPEC NOTE:  Delete 3.7 when base is specified in Division 09.

3.8	GROUNDING

.1	Install electrical ground connectors.

3.9	PROTECTION OF FINISHED WORK

.1	Protect finished access floor with:

.1	Kraft paper.

.2	0.15 mm thick polyethylene film.

.3	Seal at edges to prevent tearing.

SPEC NOTE:  Specify polyethylene film for carpet finish.

3.10	SCHEDULE

|  | Floor Finish | Location |
| --- | --- | --- |
| .1 | Vinyl Asbestos Tile: | [ ] |
| .2 | Homogenous Vinyl: | [ ] |
| .3 | Melamine Laminate: | [ ] |
| .4 | Carpet - Type I: | [ ] |
|  | - Type II: | [ ] |
|  | - [ ]: | [ ] |
| .5 | Non-Slip Rubber: | [ ] |
| .6 | Terrazzo | [ ] |
| .7 | [ ]: | [ ] |

END OF SECTION